## Bid Tab
Chiller Bid Tabulation Worksheet
(Page 1 - General Information & Evaluation Comments)
Project Information:
1. Project Name: UF IFAS Fort Pierce - Building 7305 Chiller Expansion
2. Building Owner: UF IFAS
3. IFAS Project #: 18066
Bid Submission Requirements:
1. Bids must include price for 5-year full warranty (including parts, labor, refrigerant, etc) to be considered responsive.
2. The Base Bid shall include chillers that, based on the Application Specific Part Load Value (ASPLV) calculation below, produce the same or lower ASPLV number than the target ASPLV number.
3. Attach the manufacturer's performance data supporting all data entered below, including chiller efficiencies at various condenser temperatures, as well as dimensional data for the equipment.
4. Bids must meet the both the minimum efficiency specified and must not exceed the maximum allowable dimensions to be considered responsive.
5. All Bidders are required to use the Microsoft EXCEL® spreadsheet version of this bid form and submit a printed copy. All cells highlighted in gray must be filled in for the bid to be considered responsive. The spreadsheet will automatically make all necessary calculations.
Bidder Information:
Name of Bidder
Address
City/State/Zip
Office Phone Number
Email Address
Evaluation Comments :
Chiller Bid Tabulation Worksheet
(Page 2 - Selection Criteria & ASPLV Calculation)
Selection Criteria:
Type | Description |  |  | Design Value | As Bid
General | Minimum Chiller Capacity (Tons per Chiller) |  |  | 200
| Number of Chillers |  |  | 1
| Electrical Characteristics (Volts/Phase/Hertz) |  |  | 480/3/60
Evaporator | Number of passes |  |  | 2
| EWT (Deg. F) |  |  | 54
| LWT (Deg. F) |  |  | 44
| Maximum Water Pressure Drop (Ft.) |  |  | 6
| Maximum Water Flow (GPM per Chiller) |  |  | 480
| Minimum Water Flow (GPM per Chiller) |  |  | 120
| Fouling Factor |  |  | 0.0001
| Fluid |  |  | Water
Chiller Application Specific Part Load Value - ASPLV:
Plant Load (tons) | # of Chillers Operating | % of Annual Ton-Hours | Selection Point |  | Chiller kW/Ton (1) | Weighted Efficiency (2)
|  |  | Ambient Air Temp (deg. F) | Chiller Load (tons per chiller)
200 | 1 | 15% | 95 | 200 |  | 0
150 | 1 | 30% | 80 | 150 |  | 0
100 | 1 | 45% | 65 | 100 |  | 0
50 | 1 | 10% | 65 | 50 |  | 0
[5 empty] | Bid ASPLV (3) | 0
[5 empty] | Target ASPLV | 0.63134
ASPLV Calculation Notes:
(1) Chiller kW/ton shall be based upon selection point data utilizing selection criteria.
(2) Weighted Efficiency = (% of Annual Ton-Hours) × (chiller kW/Ton).
(3) Bid ASPLV = the sum of the Weighted Efficiency column.
Chiller Bid Tabulation Worksheet
(Page 3 - Annual Chiller Operating Cost Calculations)
Annual Chiller Electric Consumption Cost:
Plant Load (tons) | # of Chillers Operating | Ton-Hours | Selection Point |  | Chiller kW/Ton (1) | Consumption Cost (2)
|  |  | Ambient Air Temp (deg. F) | Chiller Load (tons per chiller)
200 | 1 | 262800 | 95 | 200 |  | 0
150 | 1 | 394200 | 80 | 150 |  | 0
100 | 1 | 394200 | 65 | 100 |  | 0
50 | 1 | 43800 | 65 | 50 |  | 0
|  |  | Total Annual Chiller Electric Consumption Cost (3) |  |  | 0
Annual Chiller Electric Consumption Cost Notes:
(1) Chiller kW/ton shall be based upon selection point data utilizing selection criteria.
(2) Consumption Cost = (Ton-Hours) x (Chiller kW/Ton) x (Consumption Charge). The consumption charge utilized in this analysis is $0.0871, which is based on the actual electric rate structure for the building.
(3) Total Annual Electric Consumption Cost = the sum of the Consumption Cost column.
Annual Chiller Electric Demand Cost:
There are no demand charges based on the actual electric rate structure for the building. Therefore, a demand cost analysis is not required.
Chiller Bid Tabulation Worksheet
(Page 4 - Annual Pumping Cost Calculations)
Water Flow & Pressure Drop Summary:
Evaporator Pressure Drop @ As-Bid Water Flow |  |  | 0
As-Bid Evaporator Water Flow (GPM) |  |  | 0
Minimum Evaporator Flow Rate |  |  | 0
Annual Chilled Water Pumping Electric Consumption Cost:
Plant Load (tons) | # of Chillers Operating | Evaporator Flow per Chiller (GPM) | Actual Evaporator DP (FT.) | Operating Hours | Calculated Pump Power (kW) | Consumption Cost (1)
200 | 1 | 480 | #DIV/0! | 1314 | #DIV/0! | #DIV/0!
150 | 1 | 360 | #DIV/0! | 2628 | #DIV/0! | #DIV/0!
100 | 1 | 240 | #DIV/0! | 3942 | #DIV/0! | #DIV/0!
50 | 1 | 120 | #DIV/0! | 876 | #DIV/0! | #DIV/0!
|  | Total Annual Chilled Water Pumping Electric Consumption Cost (2) |  |  |  | #DIV/0!
Annual Chilled Water Pumping Electric Consumption Cost Notes:
(1) Consumption Cost = (Operating Hours) x (Pump kW) x (Consumption Charge). The consumption charge utilized in this analysis is $0.00871, which is based on the actual electric rate structure for the building.
(2) Total Annual Chilled Water Pumping Electric Consumption Cost = the sum of the Consumption Cost column.
Annual Chilled Water Pumping Electric Demand Cost:
There are no demand charges based on the actual electric rate structure for the building. Therefore, a demand cost analysis is not required.
Chiller Bid Tabulation Worksheet
(Page 5 - Annual Operating Cost Summary, First Costs, Life-Cycle Cost Calculations, & Bid Evaluation Method)
Annual Operating Cost Summary:
Annual Chiller Operating Cost (Annual Chiller Consumption Cost) | [5 empty] | 0
Annual Pumping Cost (Annual Chilled Water Pumping Consumption Cost) | [5 empty] | #DIV/0!
Total Annual Operating Cost (Annual Chiller Operating Cost + Annual Pumping Cost) | [5 empty] | #DIV/0!
First Cost Summary:
Chiller Bid Cost (each chiller excluding sales tax):
Year 2-5 Extended Full Warranty Cost
Add Alternate #1 (Surge Protective Devices)
Add Alternate #2 (Year 6-10 Extended Full Warranty Cost)
Total "Bid Evaluation" First Cost (Base Bid): |  |  |  | 0
Note: Total "Bid Evaluation" First Cost = (Total Chiller Bid Cost)+(Yr 2-5 Extended WTY Cost)
Total "Bid Evaluation" First Cost (Base Bid + Add Alternates #1 & #2): |  |  |  | 0
Note: Total "Bid Evaluation" First Cost = (Total Chiller Bid Cost)+(Yr 2-5 Extended WTY Cost)+(Add Alt #1 Surge Protective Devices)+(Add Alt #2 Year 6-10 Warranty)
Life-Cycle Operating Costs:
Total Annual Operating Cost: |  |  | #DIV/0!
Uniform Present Value Factor (UPV) |  |  | 8.84
10-Year Life-Cycle Operating Cost (Adjusted to Present Value): |  |  |  | #DIV/0!
Note: The 10-Year Life-Cycle Operating Cost = (Annual Operating Cost) x (UPV). The Uniform Present Value Factor (UPV) incorporates energy price escalation rates and the real discount rate published by the U.S. Department of Energy's Federal Energy Management Program (Source: Table Ba-3, Annual Supplement to NIST Handbook 135, 2015)
Total "Bid Evaluation" Life-Cycle Cost (Base Bid): |  |  |  | #DIV/0!
Note: Total "Bid Evaluation" Life-Cycle Cost = (Bid Bond) + (Total "Bid Evaluation" First Cost) + (10-Year Life-Cycle Operating Cost)
Total "Bid Evaluation" Life-Cycle Cost (Base Bid + Add Alts #1 & #2) |  |  |  | #DIV/0!
Note: Total "Bid Evaluation" Life-Cycle Cost = (Bid Bond) + (Total "Bid Evaluation" First Cost Base Bid + Add Alt #1 + Add Alt #2) + (10-Year Life-Cycle Operating Cost)